City of Baton Rouge

Parish of East Baton Rouge

Department of Public Works

Wastewater Treatment and Disposal Division

## PUMP STATION DEMONSTRATION CHECK LIST

(Use multiple pages if more than 4 pumps)

DATE	_______				                                  NO. OF INSPECTIONS

STATION NO: ____________________		     	          NO. OF PUMPS

GENERAL CONTRACTOR  ____ ______________	ELECTRICAL CONTRACTOR _______________

ENGINEER ________________________		PLUMBER (for RPBA)  _________________________

ELECTRIAL PROVIDER _________   METER#___________________

PRIMARY VOLTAGE ____ ___VAC  _____ Phase

WATER PROVIDER ______________   METER/ACCT NO. _______________

MOTOR VOLTAGE PUMP # 1	_____VAC	 MOTOR SERIAL NO. PUMP # 1 __________________

NAMEPLATE FLA.	_____	 PUMP MOTOR SIZE 	____  PUMP MOTOR MFG  _________________

PUMP MFG:	_____________  DISCHARGE SIZE	____	 PUMP #1 SERIAL NO. _______________

MOTOR VOLTAGE PUMP # 2	_____VAC	MOTOR SERIAL NO. PUMP # 2	_____________

NAMEPLATE FLA._______ PUMP MOTOR SIZE 		HP  PUMP MOTOR MFG	____________                          PUMP MFG:	_____________ DISCHARGE SIZE	________ PUMP #2 SERIAL NO.______________

MOTOR VOLTAGE PUMP # 3________ MOTOR SERIAL NO. PUMP # 3__________________

NAMEPLATE FLA.______ PUMP MOTOR SIZE_______HP         PUMP MOTOR MFG_______________ PUMP MFG:______________ DISCHARGE SIZE_________ PUMP #3 SERIAL NO. _______________

MOTOR VOLTAGE PUMP # 4________ MOTOR SERIAL NO. PUMP # 4__________________

NAMEPLATE FLA.______ PUMP MOTOR SIZE_______HP         PUMP MOTOR MFG_______________ PUMP MFG:______________ DISCHARGE SIZE_________ PUMP #4 SERIAL NO. _______________

Commissioning Personnel Initials: ______Owner   ______Contractor  ______ Elec Contr   ______Engr/CM

ITEM								ACTIVITY		ACTION TAKEN (IF NO)

Y/N (NA if Not Applicable)

AIR SYSTEM

- Air Compressors Operate								_______________________

- Air Line Pressure Tested: System held 60 psi

for 1 hour.  Complete prior to start up						_______________________

- Purge Automatic Functions							_______________________

- Purge Manual Functions 								_______________________

- Compressor Lead-Lag Alternates	 (bubbler only)					_______________________

- Compressor Alternates on Lead Fail (bubbler only)				_______________________

- Low Pressure (or Flow) Air Alarm Activates					_______________________

# GENERAL CONTROL PANEL

- Loss of Phase Causes Alarm							______________________

- 100% Plastabond Conduit Used							______________________

- Digital Pressure Meter Present on Panel						______________________

- Panel Heater Operates					____________	______________________

- Panel Heater Thermostat(s) Operate			____________

- Motor Digital Amp Meters Function			____________	______________________

- Alarm lights function on ALL failures			_____ ______   	______________________

- Alarm lights reset						____________   	______________________

- Site security light operates	 	                  	____________ 	______________________

- Panel Air Conditioner Operates				____________ 	______________________

- Flow Meter Functions					____________ 	______________________

- PLC Failure Simulated - Pumps Operate on

Level Floats or Switches					____________ 	______________________

- Room in panel for future SCADA transmitter		____________ 	______________________

- Seal offs installed and filled				____________ 	______________________

15- Alarm light on building/panel exterior functions		____________ 	______________________

SUMP PUMPS

# Sump Pumps Provided for Wet Well or Valve Vault	____________ 	______________________

- Sump Pumps Automatically Controlled by Floats	____________ 	______________________

- Pumps Operate Properly in Response to Floats		____________ 	______________________

- Pumps Operate Properly Via On-Off Switches		____________ 	______________________

- Pump Capacity As Specified (_____ gpm)		____________ 	______________________

- Pump ON setting if float operated			____________ 	______________________

- Pump OFF setting if float operated			____________ 	______________________

GATES AND VALVES (Complete Prior to Startup Demonstration)

- Manual valves and gates open and close properly	____________ 	______________________

- Motorized valves and gates open and close using actuator___________ 	______________________

- Override handwheel functions for motorized valves/gates___________ 	______________________

- OPEN and CLOSED lights operate properly		____________ 	______________________

- Gates leak tested and meet leakage criteria		____________ 	______________________

# Commissioning Personnel Initials: ______Owner   ______Contractor  ______ Elec Contr   ______Engr/CM

# ITEM	(Use Multiple Pages for more than 4 Pumps)	ACTIVITY	            ACTION TAKEN (IF NO)

Y/N (NA if Not Applicable)

# PUMP NO. __

1- H.O.A. Switch operates				   	____________           ________________________

2- Simulated High Winding Temp Causes Alarm					________________________

3- Simulated Seal Failure Causes Alarm						________________________

4- Pump elapsed time meter function	s						________________________

5- Pump running light illuminates							________________________

6- Pump starts on High Level Switch			            			________________________

7- Pump stops on Low Level Switch							________________________

8- Pump overload relay operates							________________________

9- Pump stops on High Head								________________________

# PUMP NO. __

1- H.O.A. Switch operates				   	____________           ________________________

2- Simulated High Winding Temp Causes Alarm					________________________

3- Simulated Seal Failure Causes Alarm						________________________

4- Pump elapsed time meter function	s						________________________

5- Pump running light illuminates							________________________

6- Pump starts on High Level Switch			            			________________________

7- Pump stops on Low Level Switch							________________________

8- Pump overload relay operates							________________________

9- Pump stops on High Head								________________________

# PUMP NO.__

1- H.O.A. Switch operates				   	____________           ________________________

2- Simulated High Winding Temp Causes Alarm					________________________

3- Simulated Seal Failure Causes Alarm						________________________

4- Pump elapsed time meter function	s						________________________

5- Pump running light illuminates							________________________

6- Pump starts on High Level Switch			            			________________________

7- Pump stops on Low Level Switch							________________________

8- Pump overload relay operates							________________________

9- Pump stops on High Head								________________________

# PUMP NO. __

1- H.O.A. Switch operates				   	____________           ________________________

2- Simulated High Winding Temp Causes Alarm					________________________

3- Simulated Seal Failure Causes Alarm						________________________

4- Pump elapsed time meter function	s						________________________

5- Pump running light illuminates							________________________

6- Pump starts on High Level Switch			            			________________________

7- Pump stops on Low Level Switch							________________________

8- Pump overload relay operates							________________________

9- Pump stops on High Head								________________________

Commissioning Personnel Initials: ______Owner   ______Contractor  ______ Elec Contr   ______Engr/CM

ITEM								ACTIVITY		ACTION TAKEN (IF NO)

Y/N (NA if Not Applicable)

RECORD WET WELL GAUGE ELEVATIONS

1- PLC or Float Low Level alarm is.		______	_________		________________________

2- Common stop is.				______	_________		________________________

3- Start Lead Pump is.				______	____  ____		________________________

4- Start 1st lag is.				______	_________		________________________

5- Start 2nd lag is.				______	_________		________________________

6- Start 3nd lag is.				______	_________		________________________

7- PLC or Float High Level alarm is.		______	_________		________________________

8- Elevation at Bottom of Air Line		______		___		_______________________

&  How Measured				______	_	___		_______________________

9- Back up low level float __ or low level 	______	_	___		_______________________

switch __ setting is.,

10- Back up high level float __ or low level 	______	_	___		_______________________

switch __ setting is.,

SUBMERSIBLE PUMPS

1- Pump travels properly on guide rails

when raised or lowered

(check prior to start up)								________________________

2- Evidence of leaks at point where pump

connects to pump base elbow							_______ ________________

3- Evidence of Pump cavitation or vortexing

4- Air release valve installed								________________________

5- Block valve at Force Main								________________________

6- Check valve limit switch 								________________________

7- Pressure gauge installed on each pump						________________________

8- Pressure transmitter installed on force main					________________________

ODOR CONTROL SYSTEM

- System checked for leaks								________________________

- Fan rotation checked and verified							________________________

- Air balance complete								________________________

- Isolation dampers open and close correctly 					________________________

- Drain traps primed								________________________

- Media loaded into vessels								________________________

- Water recirculation pump and sprays operate properly				________________________

- Nutrient feed pump operates correctly						________________________

- Make up water controls level in sump						________________________

- Media bed differential pressure is 						________________________

- Control panel operation and alarm functions verified				________________________

Commissioning Personnel Initials: ______Owner   ______Contractor  ______ Elec Contr   ______Engr/CM

ITEM								ACTIVITY		ACTION TAKEN (IF NO)

Y/N (NA if Not Applicable)

SWTCHBOARD

- Conductors color coded and labeled						________________________

- Door closure or key interlock system operates correctly				________________________

- Phasing checked on double-ended equipment					________________________

MOTOR CONTROL CENTER

- Conductors color coded and labeled						________________________

- Door closure interlock system operates correctly					________________________

- Phasing checked on double-ended equipment					________________________

METER READINGS

MEGOHM READINGS (Use Multiple Pages for more than 4 Pumps)

Pump No. 1

Leg A- GND       	______Leg B- GND    	______ Leg C- GND    __	___

A-B          ________________	B-C     ________________		   C-A        ________________

Pump No. 2

Leg A- GND       ______ Leg B- GND     ____Leg C- GND    _______

A-B        _______________	B-C        ________________	C-A     ________________

Pump No. 3

Leg A- GND  _________________	Leg B- GND  _________________   Leg C- GND  __________________

A-B _______________________	B-C ________________________	C-A _________________________

Pump No. 4

Leg A- GND  _________________	Leg B- GND  _________________   Leg C- GND  __________________

A-B _______________________	B-C ________________________	C-A _________________________

PUMPS RUNNING

Pump No. 1 (if variable speed, pump speed at 100 %)

AMP Readings:   Leg 1        ___        ________Leg 2    _____________Leg 3       ___		_

Voltage:	AB       _________VAC 	AC      __________VAC	BC      __________VAC

Pump Head: Lift from water surface to gauge ____ ft. + gauge pressure ___ psi x 2.31 = ______ feet

Calculated __ (based on wet well volume) or Measured__ Flow ________gpm

Pump No. 2 ((if variable speed, pump speed at 100%)

AMP Readings:     Leg 1         ___________Leg 2           _________Leg 3       ___________

Voltage:	AB       ________VAC 	AC      __________VAC	BC      _________ VAC

Pump Head: Lift from water surface to gauge ____ ft. + gauge pressure ___ psi x 2.31 = ______ feet

Calculated __ (based on wet well volume) or Measured__ Flow ________gpm

Pump No. 3 (if variable speed, pump speed at 100%)

AMP Readings:     Leg 1              _________   Leg 2 _______________  Leg 3 ________________

Voltage:	AB    _________VAC	AC      _________ VAC  BC        ________VAC

Pump Head: Lift from water surface to gauge ____ ft. + gauge pressure ___ psi x 2.31 = ______ feet

Calculated __ (based on wet well volume) or Measured__ Flow ________gpm

Pump No. 4 (if variable speed, pump speed at 100%)

AMP Readings:     Leg 1              _________   Leg 2 _______________  Leg 3 ________________

Voltage:	AB    _________VAC	AC      _________ VAC  BC        ________VAC

Pump Head: Lift from water surface to gauge ____ ft. + gauge pressure ___ psi x 2.31 = ______ feet

Calculated __ (based on wet well volume) or Measured__ Flow ________gpm

ITEM							ACTIVITY		ACTION TAKEN(IF NO)

Y/N (NA if Not Applicable)

# TELEMETRY SIGNALS

Data Exchange Table Submitted and Accepted					________________________

PUMP ALTERNATOR

1- After each run, Alternator switches the

Lead pump

________________________

2- Alternator switches Lead Pump

designation when designated Lead

Pump is turned Off (check each pump)		             			________________________

EMERGENCY POWER

- Breakers or ATS switch on utility failure						________________________

- Breakers or ATS switch on loss of phase						________________________

- Return to Utility source occurs on return of power				________________________

- Return to Utility source occurs on return of phase				________________________

- Delay on return of power or phase is set at 		____________ minutes

- Engine cool down timer set at 		 		____________ minutes

- Synchronizing of generators occurs properly					________________________

OTHER ITEMS TO BE CHECKED

- Access Road Complete ___ ____

- Water To Station: 	_

- Fence is complete ____

- Are there any leaks in pipes, station walls, or floor: 		_

- Are all electrical breakers and pump switches labeled: _____

- Are there any holes or wash out:

- Does the building need priming or painting inside or out:

- Are there any other items that need to done or addressed:

- Are spare parts transferred to DPW:

- Are O&M Manuals submitted:

- Has training been completed:   ___________

Provide and attach copies of manufacturer’s start up checklists, in addition to this check list, where such checklists are provided by the manufacturer’s representative.

___________						________________________

Owner							Electrical Contractor

___________	              				                                                                          Engineer

___________	_______				_________________

General Contractor							Date